## Wet Well Sizing - mph
This example calculation spreadsheet has not been reviewed or approved for wide use. It is provided as informational only. The engineer may use this information, but it should be thoroughly checked.
Pump Station Wetwell Sizing Example
Task: Determine the minimum wet well size for a wastewater pump station, wet pit only configuration, given the following:
Boxed Cells represent data inputted manually
Pumps
|  | 2 | -- | Number of Total Pumps
|  | 1 | -- | Number of Duty Pumps (no staggered cycling - one duty, one standby)
|  | 2000 | gpm | Pump Design Flow Rate (each)
|  | 125 | HP | Pump HP (each), from manufacturer's literature
Collection System
|  | 1 | -- | Number of Influent Sewers to Pump Station
|  | 6 | ft | Influent Sewer Diameter
|  | 4800 | LF | Sewer length from pump station to existing overflow point (when full)
2006-2007 hourly flow data from identical pump station and collection system
|  | 1675 | gpm | Average ADF [Average Daily Flow]
|  | 2250 | gpm | Maximum ADF
|  | 1200 | gpm | Minimum ADF
|  | 2600 | gpm | Maximum Peak Hour Flow
Identify Required Wet Well Volume Based on Cycling of Pump Motors
1. | Classify the pump station in accordance Section 6.4.2.1
|  | 2000 | gpm | Pump Station Firm Capacity
|  | SMALL | -- | Pump Station Classification based on Firm Capacity
2. | Determine Minimum Motor Cycle Time:
|  | 6 | -- | Maximum Motor Starts per Hour (see Table 6.4.2.4.1-1)
|  | 10 | min | Motor Cycle Time
3. | Calculate Required Wet Well Volume based on Cycle Time:
| V [ft^3] = | t [min] *Q [gpm]
30
where:
| t = | 10 | min
| Q = | 2000 | gpm
| V = | 667 | cubic-feet
Identify Required Wet Well Volume Based on Emergency Storage Considerations
1. | Determine Emergency Storage Minimum Detention Time:
|  | 480 | min | Based on Pump Station Classification (see Table 6.4.2.4.2-1)
2. | Determine ESF (Emergency Storage Flow):
|  | 2250 | gpm | Use Max ADF for one calendar year at identical installation
3. | Calculate Emergency Storage Volume:
|  | 1080000 | gallons | Emergency Storage Volume (Detention Time x Flow)
|  | 144385.0267 | cubic-feet | Conversion (7.48gal/ft^3)
4. | Calculate Available Capacity of Collection System for Emergency Storage
|  | 135716.8026 | cubic-feet | Available Volume of Collection System for Emergency Storage (see box sewer info above)
5. | Calculate Required Wet Well Volume based on Emergency Storage Requirements
| V = | 8668 | cubic-feet
Compare Required Wet Well Volumes from Both Methods and Use the Larger Value
8668 cubic-feet >> 667 cubic feet
The required wet volume should be 8668 cubic feet.
Note: Veriy that the wet well volume is sufficient to allow for pump movement and equipment access for maintenance.